WBF-WG “Flow Analysis” 

Draft  Technical Report
[image: image1.jpg]Qs
[ 4

WORLD BATCH FORUM






WBF-WG “Flow Analysis” 

ISA-88 Modeling using Flow Analysis

Draft 3 – September 2003

This document is a draft that represents work being done by a WBF Working Group

WBF grants permission to anyone to reproduce and distribute copies of this WBF draft, in whole or in part, but only for the following purposes and only as long as the recipient is not charged any fee for the copy (nor may the copy be included as part of a package with other materials or presentations for which a fee is charged):

1. Review of and comment on the draft standard;  

2. Provide to others for review and comment;

3. Promotion of the WG work; or 

4. Informing and educating others about the WG.

In addition, all copies must reproduce a copyright notice as follows: 


© Copyright 2001 WBF. All rights reserved. Reproduced and distributed with permission of WBF.

WBF reserves all other rights to the draft. Any other reproduction or distribution without the prior written consent of WBF is prohibited.

The reader is cautioned that this document has not been approved and cannot be presumed to reflect the position of WBF or any other committee, society, or group.  Although every effort has been made to ensure accuracy, neither WBF, members of WG, nor their employers shall be held liable for errors or limitations.

Yellow highlighting: under construction
[image: image19.bmp]
Blue highlighting: question marks, editor’s notes



WBF-WG_FA Draft on Flow Analysis

Copyright © 2001 by WBF.  All rights reserved.  Not for resale. Printed in the United States of America

World Batch Forum

107 S. Southgate Drive

Chandler, Arizona 85226

Phone:  480-893-8803
Fax:  480.893.7775

E-mail:  deann@kc-a.com     

Preface

WBF working groups provide an unbiased means for the investigation and development of work items of interest to the members.  People of like interests meet (in person or electronically) in order to delve into specific topics.  Although the topics addressed will be determined by each working group possible topics are:

· XML based batch data exchange formats

· Exception handling

· Continuation or publication of EBF working group results

· Process plant analysis based on ISA-88

· Procedure Function Chart examples

· Good practices

· Benchmarks

While the WBF will own the copyright to all WBF Working Group Reports, all working group members are given royalty free use of the WBF Working Group Reports for personal and professional purposes.  This includes use by the employers of working group members, to use work products of the working group, including any work published by the working group.

This draft technical report has been issued by the World Batch Forum (WBF), Working Group “Flow Analysis”

The following served as members of this group:

	Email
	Name
	Company
	Country

	a-smith@its-ltd.co.uk
	Anthony Smith
	INDUSTRIAL TECHNOLOGY LTD
	UK

	alain.bosatelli@eu.rhodia.com 
	Alain Bosatelli
	RHODIA
	FR

	alfonso.sancho@honeywell.com 
	Alfonso Sancho
	HONEYWELL
	

	bernard.cubizolles@isa-france.org 
	Bernard Cubizolles
	ASOPHIA
	FR

	bertrand.ricque@euraltech.fr 
	Bertrand Ricque
	EURALTECH
	FR

	dbrick@aegiscorp.com
	D. Brick
	AEGIS ANALYTICAL
	US

	dclermon@lu.danone.com 
	Dominique Clermont
	DANONE
	FR

	djoannes@danonefr.danone.com 
	Didier Joannes
	DANONE
	FR

	dror@specsoft-pfs.com
	Dror Eyal
	SPEC SOFT
	IS

	Ed.Lynch@pfizer.com 
	Ed Lynch
	PFIZER
	US

	emerson@dallas.yca.com 
	Dave Emerson
	YOKOGAWA
	US

	emol@starren.nl
	Elbert Mol
	STARREN
	NL

	eric_vitte@mail.schneider.fr 
	Eric Vitté
	SCHNEIDER ELECTRIC
	FR

	etsmrb@aol.com
	Rémi Métras
	RMB
	FR

	fl@controldraw.co.uk
	Francis Lovering
	CONTROL DRAW
	UK

	j.relland@alpha-cim.com
	José Relland
	ALPHA-CIM
	FR

	Jacky.Tachon@aventis.com
	Jacky Tachon
	AVENTIS
	FR

	Jacques.cothenet@eu.rhodia.com 
	Jacques Cothenet
	RHODIA
	FR

	jacques.grossin@adp.fr 
	Jacques Grossin
	AEROPORTS DE PARIS
	FR

	jean-francois.cardot@isa-france.org 
	Jean-Francois Cardot
	RHODIA
	FR

	jean-pierre.bovee@aventis.com 
	Jean-Pierre Bovée
	AVENTIS PHARMA
	DE

	jean.vieille@isa-france.org
	Jean Vieille* ***
	CONSULTANT
	FR

	jmrayon@jmrconseils.fr 
	Jean-Michel Rayon
	CONSULTANT
	FR

	Josef.Meixner@erls.siemens.de 
	Joseph Meixner
	SIEMENS
	DE

	jwindle@Foxboro.com
	John Windle
	FOXBORO
	US

	khaled.kassem@cran.uhp-nancy.fr 
	Khaled Kassem
	CRAN University of Nancy
	FR

	lionelcerisier@yahoo.fr 
	Lionel Cerisier
	
	FR

	mcelenk@hotmail.com 
	Metin ÇELENK
	YILDIZ Holding
	TU

	omer.akdeniz@frenchbatchforum.org 
	Omer Akdeniz**
	SINFOR AUTOMATION
	FR

	p.levrard@arcinfo.com 
	Philippe Levrard
	ARC INFORMATIQUE
	FR

	Patrick.Richard@aventis.com 
	Patrick Richard
	AVENTIS
	FR

	paul.jones@eu.rhodia.com 
	Paul Jones
	RHODIA
	UK

	pallot@ordinal.fr
	Philippe Allot
	ORDINAL TECHNOLOGIES
	FR

	quem@tpg.com.au
	Spiro Georgakopoulos
	QUEMM ASSOCIATES PTY LTD
	AU

	rdespins@foxboro.com 
	Robert Despins
	FOXBORO
	FR

	rfp@optusnet.com.au
	Robert Price
	CSL Ltd.
	AU

	smmcleod_uk@yahoo.co.uk 
	Steve MacLeod
	JACOBS ENGINEERING
	UK

	Tony@simmons.demon.co.uk 
	Tony Simmons
	CONSULTANT
	UK

	viruega@ensgi.inpg.fr 
	Jean-Louis Viruega
	ENSGI INPG
	FR

	willie.lotz@sabreweries.com 
	Willie Lotz
	SOUTH AFRICAN BREWERIES
	SA

	yong.miao@aspentech.com
	Yong Miao
	ASPEN TECH
	

	yusaksp@yahoo.com 
	Yusak Pandiana
	Technical University of Delft
	NL


*
Editor

** 
FBF WG4 chair

***
WBF “FA” WG  chair

The following companies have sponsored this work:

SCHNEIDER ELECTRIC (Draft 1)

ROCKWELL AUTOMATION (Draft 2)

SIEMENS Automation & Drives (Draft 3)

Contents

Page

121
Scope

2
references
12
2.1
Normative references
12
2.2
Other documentation
12
3
Definitions
14
3.1
Complex node
14
3.2
Confining node
14
3.3
Connection
14
3.4
Directing node
14
3.5
Equipment procedural element (EPE)
14
3.6
Flow
14
3.7
Flow Analysis
14
3.8
Flow breaker
14
3.9
Node
15
3.10
Path
15
3.11
Terminal
15
4
Overview of Flow analysis
16
4.1
A constraints based modeling
16
4.2
Intrinsically safe operational vs conventional interlocking
16
4.3
Production Plant from Flow Analysis point of view
18
5
Modeling principles and terminology
21
5.1
Basic principles
21
5.2
Modeling a process cell
21
5.3
Nodes, Terminals and Connections
22
5.4
Directing nodes and flow breakers
23
5.5
Confining nodes (CN)
24
5.6
Terminals
25
5.7
Connections
26
5.8
Complex nodes
27
5.8.1
Grouping nodes together
27
5.8.2
Nodes Breakdown principles
28
5.8.3
Grouping directing and confining nodes
29
5.9
Generic model
29
5.10
Mapping FA entities on S88 equipment entities
30
5.11
Functional view: Equipment Procedural Entities
30
6
Object model and attributes
32
6.1
Overview
32
6.2
Control Module Object Model
32
6.3
S88 Objects
32
6.4
Attributes and Properties objects
33
6.5
Path object
34
6.6
Flow object
34
6.6.1
Flow object attributes
34
6.6.2
Flow properties
34
6.6.3
Material requirement properties
35
6.6.4
Flow object operations
35
6.7
Node object
35
6.7.1
Types of nodes
35
6.7.2
Node object attributes
36
6.7.3
Node properties
37
6.7.4
Node object operations
37
6.8
Directing Node object
37
6.8.1
Directing node object attributes
37
6.8.2
Directing node properties
38
6.8.3
Directing node operations
38
6.9
Confining node object
40
6.9.1
Confining node object attributes
40
6.9.2
Confining node properties
40
6.9.3
Confining node object operations
40
6.10
Complex node object
40
6.10.1
Complex node object attributes
40
6.10.2
Complex node properties
40
6.10.3
Complex node object operations
40
6.11
Terminal object
41
6.11.1
Terminal object attributes
41
6.11.2
Terminal properties
41
6.11.3
Terminal object operations
41
6.12
Relationship object
41
6.12.1
Relationship object attributes
42
6.12.2
Relationship object operations
43
6.13
Terminal configuration object
43
6.13.1
Terminal configuration object attributes
43
6.13.2
Terminal configuration object operations
43
6.14
Connection object
43
6.14.1
Connection object attributes
43
6.14.2
Connection properties
43
6.14.3
Connection object operations
44
7
Implementing flow analysis
45


list of Figures

Page

17Figure 1: Flow integrity concern with complex networked process cells


19Figure 2: Flow Analysis conceptual view


20Figure 3: Free nodes unconnected by flow vectors


20Figure 4: Nodes and vectors making a path


21Figure 5: Process cell example 1


22Figure 6 : Nodes, terminals, connections


23Figure 7: Liquid/Gaseous nodes interface


23Figure 8: Directing nodes


24Figure 9: Ultimate directing node breakdown : Flow breakers


24Figure 10: Confining nodes


26Figure 11: Information propagation


27Figure 12: Higher level process cell modularization


28Figure 13: The whole plant as interconnected nodes


30Figure 14: Recursive Nodes - Generic model


32Figure 15: Object model


39Figure 16: Directing node control


42Figure 17 : Internal node relationships




list of tables

29Table 1: Nodes breakdown rules


29Table 2: Directing nodes attachment rules


33Table 3: Property object attributes


34Table 4: Node object attributes


35Table 5: Flow properties


35Table 6: Material properties


37Table 7: Node object attributes


37Table 8: Node properties


38Table 9: Directing node object attributes


38Table 10: Directing node properties


40Table 11: Confining node object attributes


40Table 12: Confining node properties


41Table 13: Terminal object attributes


41Table 14: Terminal properties


42Table 15: Possible node relationships


42Table 16: Relationship object attributes


43Table 17: Terminal configuration object attributes


43Table 18: Connection object attributes


44Table 19: Terminal properties




 Introduction

Although ANSI/ISA-88.01-1995 standard helps a lot in clarifying batch control, it can only be successfully implemented by experienced batch specialists. First implementations are proven to be always difficult and time consuming before taking all the benefits of S88 concepts.

Among difficulties, exception handling takes care of any situation that is not expected in normal operation when their probability of occurrence is above an acceptable level. It is often allocated as much as 80% of the design effort, leading to a huge number of discrete interlocks to prevent wrong operations.

The standard does not provide much information for the specification of Control and Equipment modules boundaries. Many S88 implementation reports raise the issue of Process Cell breakdown into its lower level components (i.e. Units, Equipment Modules and Control modules) and exception handling. From the “Top-Down” to the “Bottom-Up” through the mixed approaches, each project involves user preferences through specific, often inconsistent guidelines. 

According to Spiro Georgakopoulos and Robert Price (see 2.2 Other documentation)
“S88.01 – LIMITATIONS AND SOLUTIONS

The S88.01 standard explicitly excludes offering any specific guidance in the area of low level

decomposition. It expressly draws a line above the protective layer - “total explanation of process

segmentation is beyond the scope of this standard”. At the same time, the standard recognizes the difficulty and importance of decomposition to the whole modeling exercise -“Effective subdivision of the process cell into well defined equipment entities is a complex activity, highly dependent on the specific environment in which the batch process exists.”

A poor decomposition can be recognized by a high number of dangling control modules that the batch server must monitor and manage. In addition, methodologies which treat the protective layer separately from the process result in a large number of interlocks that need to be enabled or defeated with each phase. Either way, the modularity aspect of S88 which promises so much is compromised in a tangle of “special cases”.
There is a clear need of more practical guidelines beyond the general S88 concepts to build applications.

Flow analysis outcome is an efficient modularization that simplifies modules interactions, improves operation safety and dramatically reduces exception handling overhead. It may apply to any control models, however this report considers its application within S88 models.

The purpose of the WBF Flow Analysis Working Group is to develop guidelines based on current practices to complement S88 models to enforce physical and equipment procedural model design.

Editor’s note:

Not sure it corresponds to the current scope
This work is intended to help people from process design, operation and process control communities to well understand these concepts and to communicate together, producing robust and safe applications on a consistent basis. 

It should also help vendors to develop supporting tools based on consensual concepts.

BATCH CONTROL

ISA-88 Modeling using Flow Analysis

1 Scope

This report focuses on design requirements for inherent actuators interlocks based on flow analysis. It addresses :

· Process cell equipment breakdown (typically at the Control Module level)

· Exception handling at the process actuator level

Other subsequent reports may develop other aspects of flow analysis in S88 control design.

The expected results will be an S88 compliant guideline to address specific issues encountered in actual implementations of the standard. The expected benefits are:

· Control Modules breakdown consistency leading to a high level of reusability

· Improvement of operation safety 

· Easier Exception Handling 

2 references

2.1 Normative references

The following normative documents contain provisions, which through reference in this text, constitute provisions of this part of this report. At the time of publication, the editions indicated were valid. All normative documents are subject to revision, and parties to agreements based on this part of this standard are encouraged to investigate the possibility of applying the most recent editions of the normative documents indicated below. Members of IEC and ISO maintain registers of currently valid normative documents.

IEC60902:1987, Industrial-process measurement and control : Terms and definitions
IEC61512-1:1997, ANSI/ISA-88.01-1995, Batch control- Part 1:  Models and terminology

IEC61512-2:2001, ANSI/ISA-88.00.02-2001, Batch control - Part 2: Data Structures and Guidelines for Languages.

Note :

In this report, the ANSI/ISA-88 standard will be referred to as S88.

2.2 Other documentation

The following documents are related to existing flow-based methodologies. Although the present report uses fundamental elements from this documentation, it may not comply with the terminology and features used or expressed in them. However, the reader may find helpful information about the genesis of the methodology.

· “Methodological guide for the analysis of multipurpose batch process plants” RHONE-POULENC N° 501/93.875 - GET 5/EM/519/97/1119 - GT ASTRID

· “DELTA NODES Automated flows methodology” JMR Conseils N° JMR86/R01-2001_v3

· “A Flow Stream Approach for Process Cell Modularization” - By François Lebourgeois (Rhône Poulenc), Jean Michel Rayon (JMR Conseil) and Jean Vieille (Consultant) - Presented at the World Batch Forum Conference in Atlantic City (NJ, USA) on 23/04/2000

· “The Missing Link – A generic process control model” - By Spiro Georgakopoulos and Robert Price (Quemm Associates Pty Ltd) – Presented at the 6th World Congress of Chemical Engineering in Melbourne, Australia on 23-27 September 2001

· BatchML XML schemas developed by the World Batch Forum.

Definitions

For the purposes of this part of this report, the following definitions apply. All terms defined here are italicized in the text when their use corresponds to the definition. Abbreviations are included in the definitions. They are capitalized in the text.

2.3 Complex node

is made of several nodes of both directing and confining types.

2.4 Confining node

has the ability to contain the flow.

2.5 Connection

links nodes together through their terminals. It is not an equipment entity (as to flanges assembled together, each flange being owned by its corresponding node)

2.6 Directing node

has the ability to control the flow (direction or confinement).

Directing nodes support inherent interlocks that prevent erroneous automatic or manual handling according the safety needs.  
2.7 Equipment procedural element (EPE)

Equipment procedural element is extensively addressed in S88 part 2. However, it is not formally defined in the current edition of S88.

Equipment procedural element is an element of the part of the S88 procedural model , which applies to equipment control. It can by either a procedure, a unit procedure, an operation, a phase or any user defined procedural entity. Its equivalent at the recipe side is the recipe procedural element.

2.8 Flow

the material or energy content in a path, i.e. the stream of product or energy that takes place within a set of equipment working together on it

2.9 Flow Analysis

a methodology based on an analytical review of processing equipment that aims at modeling equipment entities in a way that allows generic mechanisms to impose critical actuators to operate within specified constraints.

It is safety-focused, providing self-immune environment against automatic control and manual operation errors regarding material and energy handling.

2.10 Flow breaker

a device that has the ability to break the flow. It can be part of a directing node, part of a complex node, or an elementary directing node.

2.11 Node

a consistent equipment entity. It can correspond to any S88 equipment entity (Control module, equipment module, unit, process cell…), but would generally comply with Control Modules. It can be confining, directing or complex (mixed and embedding other sublevel nodes)

2.12 Path

the collection of nodes assembled to perform a functionality provided by an equipment procedural element. A path can support one or several flows.

2.13 Terminal

is the physical interface of a node
Overview of Flow analysis

2.14 A constraints based modeling

Process equipment is selected and installed with a clear expectation of the purpose it will serve in terms of physical and chemical processes it is to encounter. A process modeling exercise must recognize those constraints and incorporate them.

A critical constraint is the requirement that the material remains confined within a specified part of the process equipment. The operating context dynamically defines which part of the process equipment is allocated to each executing process oriented functions. A key performance measure of an operating process plant is how well material is contained within the process.

In selecting the equipment a number of physical and safety constraints are imposed, beyond which it cannot operate. In a plant as a whole, additional constraints derived from the interaction of equipment come in to play. 

Finally, the product being processed will induce additional safety and operational constraints.

These constraints can be categorized as follow:

1. Equipment constraints may be physical things like capacity, maximum operating temperature, pressure, volume or flow. Or they may be a chemical (material) constraint – a vessel must never process material with pH less than 5. Or they may relate to hygienic status, etc. 

This information is attached to the equipment
2. Product constraints include things such as maximum temperature, blending compatibility.

This information is attached to the product

3. Relational constraints between equipment, between products or between equipment and products. For example, possible connections between equipment determine assembling constraints; 2 products may be incompatible and shall never be in contact; a product may not be processed by certain equipment…

2.15 Intrinsically safe operational vs conventional interlocking

The following simple example below illustrates how flow analysis impacts on control system implementation and operational safety considering the confinement control aspect. 

This example shows the difficulties that have to be faced of when dealing with flexible process cells to avoid cross contamination or pollution by opening a valve which does not contribute to the intended functionality (here, transferring product from T2 to T8).


[image: image2.wmf]T1

T2

PA

T3

T4

PB

T5

T6

T7

T8

Vi1

Vi3

Vi2

Vi4

Vi5a

Vi6a

Vo1a

Vi7a

Vi8a

Vi5b

Vi6b

Vi7b

Vi8b

Vo1b

Vo2a

Vo2b

Vo3a

Vo3b

Vo4a

Vo4b


Figure 1: Flow integrity concern with complex networked process cells

Such process layout imposes to implement a protective layer, which must be effective when the operator manually controls the plant as well as in automated operation to avoid errors when controlling the different circuits.

In order to protect the circuit “A” transferring product from T2 to T8, valves Vo1a, Vo2b, Vo3a, Vo4a, Vi5a, Vi6a, Vi7a, Vi8b are to be forced to their closed position.

A conventional approach begins by a very detailed risk analysis and ends by 

1) a huge list of interlocks such as :

IF PHASE “TRANSFER T2->T8” IS ACTIVE THEN


Vo1a FORCED CLOSE


Vo2b FORCED CLOSE


…

2) an equivalent set of starting conditions for phases:

INITIALIZING PHASE “TRANSFER T2->T8”


CHECK Vo1a CLOSED


CHECK Vo2b CLOSED


…

3) coordination control to suspend the phase if one of these valves fail

This extensive analysis, specification and coding must be performed for each combination.

Conventional approaches propose to simplify this design by interlocking phases instead of valves. However, this method constrains the operation flexibility, and does not prevent a wrong manual operation. Initial conditions / actuators failures are to be controlled anyway.

As an example, the following values were noted in a typical multipurpose chemical process cell:

· Number of units / shared equipment modules: 34

· Number of phases: 180

· Number of instruments: 600

· Number of interlocks: 1700

· Number of interlocks combinations: 13000

Flow analysis provides intrinsic, extensive interlocking for providing a better level of circuit integrity control than these numerous interlocks without any additional coding. 

Conventional interlocking seldom reaches a high level of safety because of its exponential complexity. These interlocks may be dramatically affected when adding new equipment or defining new phases. (The number of combinations corresponds to the number of cases that are to be considered when adding/modifying equipment or phases.)

Smart designers implement matrices to define these interlocks. Coding becomes better, however other issues remain.

Finally, the validation effort is directly affected by the number of checks to ensure the system will behave as designed. Replacing discrete interlocks by a single validated FA mechanism dramatically reduces this effort.

2.16 Production Plant from Flow Analysis point of view

Flow analysis is directed at looking at physical (people, material, energy) flows. It does not address financial, or information flows.
· A production plant uses, moves, acts on 2 basic flows:

· Material flow
· Energy flow
· … using suitable equipment

· Liquid material: Pumps, valves, pipes, vessels

· Solid or Packed material: conveyors, lifts

· Powdery material: roots, pipes, conveyors

· Electrical energy: cables, bus bars, transformers, breakers

· Thermal Energy (i.e. steam):  pipes, exchangers…

· Mechanical energy: agitators

· …

· … performing specific or more complex process oriented functionality 

· Charging, Emptying, Filling, Distillation, Filtering

· Heating, stirring, 

· …

These actions 

· may have an implicit (i.e. charge a vessel, which end when the requested quantity is obtained) or an explicit ending (heating, stirring… which run forever until they are requested to stop). 

· may act on a single flow (charge, stirring), on several flows (in-line mixing)

· may use one flow to act on another one (heating)

Any production system (i.e. a process cell) can be considered as a set of “closed sections” regarding the different material or energy flows that can occur into it (e.g. reactors, filters, pump sets). These closed sections are bounded by flow breakers (e.g. valves), which control their linkage with other sections.

Note :

Some parts of the production system cannot be considered as closed locally, but rather as infinite capacities that supply or consume product or energy. They represent Process Cell connections to raw or finished material, ancillary fluid or utilities (Sources and Sinks on the diagram).
Whatever is the part of the plant to be considered, any production system can be viewed as follow:


[image: image3.wmf]Material 

/ 

Energy 

Sources

and sinks

Energy Sources

Energy Sinks

Material Sources

Material Sinks

A

D

B

E

F

C

E

Nodes

Material 

/ 

Energy 

Flow vectors


Figure 2: Flow Analysis conceptual view

The considered part of the plant (the studied production system) appears as a set of material and energy networks:

· Sources and sinks are the connection points that limit the scope of the analysis

· Nodes are the places were material or energy is transformed, stored, directed. They are actual equipment such as vessels, reactors, transformers, exchangers, pipes, valves, pumps, conveyors...

· Flow vectors indicates how the pieces of equipment are actually connected. The connections established by flow vectors define the actual plant layout. It may be fixed, but it may also be dynamically arranged for the purpose of the actual product processing requirements. The figure below shows free nodes that are not yet connected: equipment is available, but disconnected (imagine it lies disconnected on the workshop floor) and unable to fulfill any process oriented functionality (no material nor energy can be processed). It is not presumed to be assembled in a particular shape until it is used to make something. Flow vectors do not currently connect the equipment. They are waiting for any future usage.


[image: image4.wmf]Material 

/ 

Energy 

Sources

and sinks

Energy Sources

Energy Sinks

Material Sources

Material Sinks

A

D

B

E

F

C

E

nodes

Material 

/ 

Energy 

Flow vectors


Figure 3: Free nodes unconnected by flow vectors

· A process functionality requires the support of a path by allocating several adjacent nodes (connected by flow vectors). The figure below shows the path P1 assembled to perform a process functionality using nodes A, B, F.  


[image: image5.wmf]Material 

/ 

Energy 

Sources

and sinks

Energy Sources

Energy Sinks

Material Sources

Material Sinks

A

D

B

E

F

C

E

nodes

Material 

/ 

Energy 

Flow vectors

P1

P1

P1

P1


Figure 4: Nodes and vectors making a path

Modeling principles and terminology

2.17 Basic principles

Analyzing flows in a process cell may be done at different level:

· The connection analysis reveals how equipment is actually linked depending of flow breakers and connections statuses

·  The static analysis concentrates on motionless flows, in order to check if static conditions allows the flow to occur (i.e. to open the corresponding flow breaker). It gives up once an actual flow is established. 

· The dynamic analysis focused on operating flows to compare the actual performance to internal models in order to detect abnormal deviations and to predict expecting physical conditions.

This report focuses on operation safety, checking the conditions before the flow occurs to allow a flow breaker to open or a directing node to operate as requested. It is based on connection and static analysis. 

2.18 Modeling a process cell

The following figure shows an example of a simple process cell from which basic concepts, terminology, and modeling rules can be presented.


[image: image6.wmf]CN1

CN2

CN3

CN4

CN5

B1

B2

B3

B4

B5

B6

B7

B8

CN :

Confined Nodes

DN :

Directing Nodes

B :

Flow Breakers

T : 

Terminals

DN1

DN2

DN3

B9

DN4

DN5

DN6

T1

T2

T1

T2

T1

T2

T1

T2

T3

T1

T2

T3

T4

T1

T2

T3

T1

T2

T1

T2

T1

T2

T1

T2

T1

T2

B10

DN7

T1

T2


Figure 5: Process cell example 1

This process cell includes the following equipment:

· 3 main processing equipment (CN1, CN4, CN5) that could be qualified as units following S88 definitions.

· 2 in-line processing equipment (CN2, CN3) that could be qualified as equipment modules following S88 definitions.

· valves or group of valves (DN1-DN7) that could be qualified as control modules following S88 definitions. These valves are represented as no-way symbols but they can be removable pipes and/or blind flanges as well.

2.19 Nodes, Terminals and Connections


[image: image7.wmf]Node

Terminals

Node

Connection


Figure 6 : Nodes, terminals, connections

All identified pieces of equipment are nodes which: 

· Represent the recipient (the physical equipment) and its content (the product or energy inside)

· Have an informational interface provided by

· properties attached to the recipient (equipment statuses and capability, product id…)
· properties attached to the content (physical and chemical conditions)

· May have a behavioral interface provided by methods or functionalities that can be invoked by other entities

· Have a physical interface provided by terminals, which

· hold specific properties and statuses,

· can be linked to together by connections.
Node categories

Nodes can be categorized to address generic set of constraints and specific modeling rules. For example Astrid / Delta Nodes identifies the following categories:

· Energy

Controls energy through the equipment (Reactor heating jacket, energy side of an exchanger, vacuum system, agitator)

· Utility


Corresponds to common resources delivering or receiving fluids or energy to or from the process cell. It has no direct contact with the product being manufactured. It is generally shared by several Units or Process Cells (Compressed Air supply, N2 distribution, waste collection, venting system…)

· Material 

Participates to the product transformation or movement (Pipe, tank, reactor, transfer line, conveyor, product side of an exchanger…)

Sub types of material can be defined. This can help to distinguish different flows through the same equipment:

· Solid

· Liquid

· Gaseous

· Powdery

· …

For example, the liquid side (lower part) of a reactor is member of the “Material/liquid” node that can hold the product, while the gaseous upper part of the reactor is member of the “Material/gaseous” node controlling the pressurization. This allows dealing with 2-chemical phases equipment in order to allow parallel control using separate equipment procedural elements. Exclusive node allocation does not compromise functional flexibility.


[image: image8.wmf]Nitrogen

Atmosphere

Product 

in

Product 

out

N2

N1

N1 : 

Material

/

Liquid node

N2 : 

Material

/

Gaseous node

Flow 

break


Figure 7: Liquid/Gaseous nodes interface

Node types

There are 3 types of nodes:

· Confining nodes which contain the flow 

· Directing nodes which control the flow by their embedded flow breakers
· Complex nodes which combines both confining and directing nodes
2.20 Directing nodes and flow breakers

Directing nodes (DN) have the ability to control the flow (breaking, directing). They generally cannot retain the flow inside themselves. 


[image: image9.wmf]B2

B3

B4

DN2

T1

T2

T3

T4


Figure 8: Directing nodes

They embed flow breakers that actually control the flow. Flow breaker can be the lowest possible breakdown of directing nodes. The following figure develops the previous one into elementary directing nodes encompassing single, simple flow breakers.


[image: image10.wmf]DN2

T1

T2

T3

T4

B1

DN1

T1

T2

B1

DN2

T1

T2

B1

DN3

T1

T2


Figure 9: Ultimate directing node breakdown : Flow breakers

Depending on the user’s choice, directing nodes can be defined at the appropriate breakdown level (Figure 8 versus Figure 9). 

Several directing nodes can be linked together to form a more complex flow control equipment.

Flow breaker can be controlled remotely or manually. They are devices such as

· one-way valves, multi-ways valves 

· liquid / gas interface 

· feeder or conveyor motor

· removable pipes, blind flanges or plugs

· doors or windows, 

· traffic lights or mobile bridges

· …

2.21 Confining nodes (CN)

Confining nodes do not control the flow, but can contain it. They do not embed flow breakers, though they can influence the flow by embedded devices such as pumps or control valves. 

All terminals of a confining node are “statically equipotent” i.e. if the flow doesn’t move and the node is not running any material or energy transformer, all physical conditions are the same for all connections (static analysis). This is generally not completely true: hydrostatic weight can influence the pressure depending of the altitude of the terminal. Also, the temperature can be different at different places and different times. The Figure 10 shows 2 different examples. 


[image: image11.wmf]CN1

T1

T2

T3

CN2

T1

T2

T3


Figure 10: Confining nodes

Confining nodes can be combined into a bigger confining node. 

2.22 Terminals

Terminals represent the physical interface of nodes. Nodes can be connected to each other by their terminals linked by connections.

Terminals can be:

· Inputs, if they can only receive an incoming flow
· Outputs, if they can only send outgoing flow
· Bi-directional if they can send or receive flow either.

Terminals can have other characteristics such as:

· type and size of connection mean (flange)

· Physical limits (max. pressure and temperature

· …

Directing nodes terminals have a particular “Flow” attribute that control the flow occurrence. This attribute has 2 values:

· Open

· Close

The “close” state means the terminal is a dead end. The flow does not go further. Flow breakers that are responsible for this state look at the terminal information to accept an opening order.

The “open” state means the directing nodes has established a way out for the flow toward another node, and there is at least one way toward a confining node (i.e. the flow can occur between 2 confining nodes). 

Terminals are fundamental in referencing information relative to:

· the equipment they are attached to 

· the product which flows through them: Product related information is acquired from the terminals to terminals relationships attached to the node for output terminals, or from other terminals through its connection to outside equipment for inputs. 

Finally, flow breakers will operate under safe conditions that are assessed by looking at the information available at its terminals
The Figure 11 below shows information propagation through terminals. Flow breaker B1 is supposed to be closed. Because the ultimate goal is to protect operation from erroneously opening a flow breaker, there is no point to consider information propagation between communicating nodes (static analysis). We only need to propagate information at the flow breaker terminals from the corresponding confining nodes. Once the flow breaker has been opened, the resulting flow is no longer considered, and the terminal information is not requested anymore.


[image: image12.wmf]CN1

T1

T2

CN2

T1

T2

T3

B1

DN3

T1

T2

Node 

Actual

Pressure = 1.12 Bar  

Actual Temp

= 65C

Actual Product

= 

Water

Actual Quantity

= 255 L

Design Pressure = 2.2 Bar

Design 

Temperature 

= 120C

Capacity

= 855 L

Output Terminal

T2_Conditions = CN1_Condition

Input Terminal

Status

=

Blocked

T1_Conditions = T2_Conditions

Connection

T3.CN1 => T1DN3

Output Terminal

Status

=

Blocked

T2_conditions 

= CN2.T1_Condition

= CN2_conditions

Connection

T3.CN1 => T1DN3

Node 

Actual

Pressure = 1.00 Bar  

Actual Temp

= 25C

Actual Product

=

Water

Actual Quantity

= 0 L

Design Pressure = 6 Bar

Design

Temperature

= 120C

Capacity

= 0 L

Output Terminal

Connected 

terminal DN3.T2=

Blocked 

=>

T1_Conditions = CN2_Condition

CN1

DN3

CN2

Actual 

condition 1

Actual 

condition 2


Figure 11: Information propagation

2.23 Connections

Nodes can be connected to each other using connections that link terminals to each other.

· In many cases, the process cell layout and its connections are fixed.

· In other cases, connections are built at run time depending of the process to be executed.

Connections represent the fact that 2 physical entities (terminals) are purposely and adequately attached to each other. They aren’t physical objects:

· A pipe which links 2 equipment is part of the confining node it is attached to (the side which is connected without valve). 

· A removable pipe used to connect 2 pieces of equipment, is considered as a directing node with 2 terminals.

Connections shall fulfill the following requirements: 

· All confining nodes terminals are to be connected to either another directing node.  This allows the process to containing the flow, because it guarantees that it is bounded by flow breakers.

· Connections can only link compatible terminals: 

· Terminals can be input, output or bi-directional

· An input terminal can be connected to only one output terminals
· An output terminal can be connected to several input terminals
· A bi-directional terminal has to be properly connected according its current use

· Connected terminals shall have compatible characteristics

The main role of a connection is to link terminals in order to let the nodes communicate the actual process conditions downstream the flow.

2.24 Complex nodes

2.24.1 Grouping nodes together

In the previous example the process cell was broken down in elementary pieces were elementary flows can be revealed.

The concept of nodes is flexible and can describe any physical hierarchy. For example, the following figure represents the same process cell, but identifies “macro nodes”, which are consistent with the mechanical engineering (each node corresponds to separately engineered modules, or skids delivered by different subcontractors)


[image: image13.wmf]N1

N2

N4

N3

B1

B2

B3

B4

B5

B6

B7

B8

N : 

Nodes

B :

Flow Breakers

T : 

Terminals

B9

T1

T2

T2

T1

T3

T3

T4

T5

T3

T1

T1

T1

T2

B10

T2


Figure 12: Higher level process cell modularization

Complex nodes do not allow the best flexible and accurate flow management (for example to deal with bi-directional connections), because the relationships between terminals are too complex to be efficiently modeled. However, if bounding flow breakers are identified as nodes, it becomes possible to control incoming and outgoing flows. This may be useful when integrating packages.

Complex nodes are obtained by increasing the modularization granularity (see 5.8.2). It dramatically simplifies the control system implementation by reducing the number of modules. 

At the highest level, a plant may be analyzed the same way :


[image: image14.wmf]Raw material storage area

Power

Water

Raw

Materials

Heat

Smoke

Waste water

Finished

goods

Power 

generation and

utility distribution

Process 

cell 

1

Finished goods storage area

Fuel

Waste 

collection 

and disposal

Process 

cell 

1


Figure 13: The whole plant as interconnected nodes

2.24.2 Nodes Breakdown principles

Material or energy flows are supported by Paths. A node represents a part of a Path, acting as a container of material or energy. The breakdown of the facility into nodes is made by applying the following rules:

· Breakdown rules (BK) give guidance to split the process cell in nodes. Strictly applied, these rules leads to the most refined breakdown and results in the highest number of nodes
· Aggregation rules (AG) give guidance to possibly reduce the number of nodes (end the subsequent control system complexity) in grouping equipment entities that form a set of equipment, which works independently.

The following table presents the rules that can be applied at the lowest breakdown level (the nodes the control system will have to deal with, regardless they are combined together to form higher level entities). 
	Rule
	Type
	BK
	AG
	Description, Comments

	Closed (confined) section 
	Confining
	X
	
	A node is bounded by flow breakers
Example, this rule is mentally applied to piped installation by “blowing” in any part of the cell while flow breakers are operating (valves are closed). The identified node is the under-pressure part of the cell.

	Flexibility


	All
	
	X
	When grouping nodes, the resulting diminished flexibility shall be challenged by checking if different parts of the same node could be used by different phases at the same time.

	Inter-CMs Constraints 


	All
	
	X
	Aggregation releases constraints enforcement between aggregated nodes.

A coarse breakdown may lead to lose the benefit of secured operation, which is basically the intent of the Flow analysis.

	Reusability
	All
	
	X
	Looking for reusability suggests to isolating equipment subsets that are fully standards and match the actual equipment once assembled.

The number of different nodes increases with aggregation. The designer shall compromise between reusability and the number of nodes.

	Virtuality


	Confining
	X
	
	It is sometime difficult to identify the equipment the node represents. That could be the case for controlled physical measurement that are not part of any mechanical part of the equipment acting on one or several actuators. (Example: a remote vision system) 


Table 1: Nodes breakdown rules
2.24.3 Grouping directing and confining nodes 

It may be convenient to group confining and directing nodes in complex nodes that can be consistently managed as autonomous equipment entities (Control Modules). As a side result, directing nodes are seldom found as separate entities. An outstanding drawback of this grouping is that it cannot comply with bi-directional and merging flows. 

The resulting complex nodes forms the S88 control module layer or the Astrid / Delta Node Resource layer. The following table proposes the rules to attach a particular directing node to the appropriate confining node.

	Attachment Rule
	Node Type
	Comment

	Upstream driven
	Material

Sky
	This rule applies to finite nodes corresponding to process related flows.

The directing node is attached to the upstream confining node considering the flow direction.

	Process side driven
	Energy Utility
	This rule applies to nodes that control a shared utility to the process.

The directing node is attached to the process side confining node whatever the direction of the utility fluid is.


Table 2: Directing nodes attachment rules

2.25 Generic model

Nodes are connected to each other, and embedded within higher-level nodes.

Depending on the primary breakdown, nodes can be elementary confining or directing nodes, as well as combined directing nodes or complex nodes.

Nodes hierarchy and internal relationship is modeled until the lowest-level defined nodes. At the lowest level, it becomes a black box with terminal internal relationships.


[image: image15.wmf]Ny2

Ny6

Ny3

Ny5

Ny4

Ny1

T3

Nx1

T1

T2

T3

Nx2

T1

T3

T2

T4

T5

T1

T2

Nz1


Figure 14: Recursive Nodes - Generic model

2.26 Mapping FA entities on S88 equipment entities

As shown above, any physical entity can be interpreted as a node. All S88 equipment entities physical can be represented as nodes whatever is their level in the S88 physical model.

The application field of the flow analysis is widely open. However, for the purpose of this report, we will concentrate at the lowest physical level where the flows are actually controlled, in order to support the protective layer that will secure the actuator operation.

Typically, the finest nodes breakdown will correspond to Control Modules.
2.27 Functional view: Equipment Procedural Entities 

In order to make a product, a production system must:

1. Provide the required basic process functions its equipment is capable of doing (EPE, equipment procedural element). In S88 EPEs can be Phases, Operations, Unit Procedures, Procedures.

2. Orchestrate these EPEs following the product processing rules (Recipes, made of Recipe Procedural Elements or RPEs)

This is the S88 concept of separation between equipment control and process control. flow analysis may interprets EPEs as follow (the term node is replaced by control module :

· In order to execute a specific EPE, the needed control modules (initially considered lying dismantled on the floor) need to be assembled to establish a path. The path represents the physical extent of its execution and is exclusively allocated to its initiating EPE. 

· An EPE can execute only if its path can be initialized i.e. the corresponding Control Modules are available to its use - not currently used by another EPE allocating an overlapping path or disabled for whatever reason - and the necessary connections are feasible.

· A path may enable one or more flows. Any combination of flows in a path is allowed from the control point of view; however, it should be consistent with the mechanical reality (connection check).

As stated in the scope section, this report only concentrates on the protective layer and basic control. The functional (procedural) aspects will not be further discussed here.

Object model and attributes

2.28 Overview

When dealing with an actual application, designers may take benefit of flow analysis to help modeling and implementation. Examples of applications examples are given in annexes.

This section presents the detailed FA elements in order to facilitate design and implementation.

2.29 Control Module Object Model

[image: image16.png]1.2[ sesere

s68_Procedure | [s8_unitProedure| [ soe_operation 38 _Phase o8 _UserErE
Flow = - Patn
s58_EqptEnity
1
<t
558 _contronosute] [ss8_Equipmentitoaute] [ ses_umit 558 _Procescel | [ 585_UserEqptentty
ap e o Jlas
ateriaiReq_propery] [ _Flom_Propety Node
Diresting Node Complex Node Confining_Nods
o.s he
Node_Propety Relationship
e & pr lo-
Ditectingtiods_Propery Confininghode_Property
1 he
Comnestion 87 0 Tuminar Teminl_Confia
@ o
Connestion_Propery Teminal_Praparty





Figure 15: Object model

2.30 S88 Objects

The object model starts by the S88 equipment entity, which is specialized into control module type, equipment module type, unit type or process cell type, as well as any user defined level (extensibility of S88 models).

Whatever they are, S88 entities may be associated to nodes. 

Note : Another option could have been to merge S88 Equipment Entity and Node concepts, which are pretty similar.  However, such an approach would have been more complex because types of nodes would have overlapped with S88 physical level. It also allow flow analysis concept to be used with different concepts than S88.

The corresponding objects are not defined in this report:

· S88_EqptEntity

· S88_ControlModule

· S88_EquipmentModule

· S88_Unit

· S88_ProcessCell

· S88_UserEqptEntity

· S88_EPE

· S88_Procedure

· S88_UnitProcedure

· S88_Operation

· S88_Phase

· S88_UserEPE

2.31 Attributes and Properties objects

In the model each object has a set of generic attributes. These attributes may be optional or required.

Note :

Data types are not defined, interoperability is not address in this report (and shall not be a concern within the scope of this report). 

Properties are process related information. All property objects are based on the same meta-class

	Property meta-class object attributes

	Attribute Name
	Description
	Examples

	ID
	An identification of a property of the associated object.
	

	Description
	Contains additional information and descriptions of the property.
	

	UOM
	The unit of measure of the associated property value, if applicable.
	

	DesignValue
	Design or typical value, set of values, or range of the property.
	

	CurrentValue
	Current value of the property
	

	MaxValue
	Maximum value of the property
	

	MinValue
	Minimum value of the property
	


Table 3: Property object attributes
This meta-class defines the design information (design, maximum and minimum values), as well as the current value of the same information. This is the basic information to check flow consistency by comparing design and actual values:

· design value of the node at the downstream side of a flow breaker against actual value of the node at the upstream side of the flow breaker

· Actual and design values within the same equipment

The following classes are based on this meta-class:

· Flow_Property

· Material_Property

· Node_Property

· DirectingNode_Property

· ConfiningNode_Property

· Connection_Property

· Terminal_Property

Properties can also be used for additional information as a mean to extend the model without compromising its consistency and easily identify user / implementation specifics.

2.32 Path object

The path establishes the relationship between a flow and the nodes.

Editor’s note:

Do we need the path object?
2.33 Flow object

A flow shall correspond to an S88 equipment procedural entity, which is the S88 equipment process oriented functionality. (Astrid / Delta Nodes gives use both “Functions” and “Flow” terms do designate the functionality and the flow which is built to uniquely support it).

This object is presented on the model, because it holds material requirement properties, which are needed to control the proper conditions of the allocated nodes.

Nodes are actually acquired by flows at run-time. If the acquired node is made of lower level nodes, the owning flow information is propagated downstream in the hierarchy, allowing any node to control its current conditions against material requirements.

In actual implementations, several EPEs may run together to form a given flow. It is the case when a TRANSFER phase is synchronized with a RECEIVE phase on 2 different units. This is represented by a flow containing 2 lower-level flows, each of them being associated to the corresponding phase.

Flow is a recursive structure, and each flow may be related to 0 or several EPE.

2.33.1 Flow object attributes

	Node object attributes

	Attribute Name
	Description
	Examples

	ID
	An identification of the object.
	

	Description
	Contains additional information and descriptions of the object.
	

	S88_ProceduralLevel
	Specifies the S88 EPE procedural hierarchy level
	Possible values are:

· Procedure

· Unit procedure

· Operation

· Phase

	BatchID
	Batch identifier. 
	

	Product ID
	Product identifier
	

	OperatorID
	Operator Identifier.
	

	ActivationStatus
	Activation status of the flow.
	Possible values are:

· IDLE

· RUNNING

· STOPPED

· HOLD

· FAULT

	ActivationSubStatus
	Additional identifier, documents the ActivationStatus. (Application specific values) 

It identifies specific running behaviors or mitigation methods
	


Table 4: Node object attributes

2.33.2 Flow properties

To be completed

	Example of flow properties

	Property  Name
	Description
	Examples

	
	
	

	
	
	


Table 5: Flow properties

2.33.3 Material requirement properties

Material requirement information is attached to the flow because this information is defined in the recipe and has to be downloaded into EPEs/flows at run-time. It propagates from the Recipe Execution domain to the operating EPE/flow and finally to the acting control modules to feed flow control interlocks.

	Example of material properties

	Property Name
	Description
	Examples

	Quantity
	Quantity of product to be processed
	

	Specific mass
	
	

	SizeL
	
	

	SizeW
	
	

	FlowRate
	Required flow
	

	Temperature
	Required Temperature
	

	Pressure
	Required pressure
	

	PH
	Required PH
	

	…
	Note : 

Other attributes may be defined by the user
	


Table 6: Material properties
2.33.4 Flow object operations

Any flow can have incorporated operations that can be invoked for performing procedural control as EPEs.

There are no specifics regarding flow analysis regarding procedural control.

2.34 Node object

2.34.1 Types of nodes

Nodes can be specialized in 2 types: directing nodes, confining nodes.

Node structure is recursive; a node can be made of other nodes:

· Directing nodes can content other directing nodes. At the last level, they content flow breakers
· Confining nodes can content other confining nodes
· A complex node is made of both type of nodes
Information attached to the node (attributes or properties) is mainly equipment related. 

Node object attributes

	Node object attributes

	Attribute Name
	Description
	Examples

	ID
	An identification of the object.
	

	Description
	Contains additional information and descriptions of the object.
	

	S88_EqptEntity
	Corresponding S88 equipment entity
	

	S88_EqptLevel
	Specifies the S88 physical hierarchy level. 
	Possible values are:

· Control Module, 

· Equipment module, 

· Unit, 

· Process Cell

	ContainedIn
	Node this node is contained in
	

	Type
	Type of the node. 

The complex type can be self-specified if the node contains both type of nodes or a complex node.

It has to be specified if the breakdown does not model the node components.
	Possible values are: 

· Confining

· Directing

· Complex

	Category
	· Category of the node. 

Other values can be defined in properties
	Possible values are:

· Material/Powdery

· Material/Liquid

· Material/Solid

· Material/Gaseous

· Energy

· Utility

	BatchID
	Batch identifier. 

· It may be set by the owning EPE and shall propagate downstream in the node hierarchy

· It may by set by the directing nodes terminals and shall propagate upstream in the node hierarchy. Multiple batch identifiers may result in flow merging depending on the node composition and equipment usage 
	

	ProductID
	Identifier of the last product the node contained
	

	FlowID
	The flow  identifier is set by the acquiring EPE.

It propagates downstream in the node hierarchy.
	

	OperatorID
	Operator Identifier.

It is set by the owning EPE

It propagates downstream in the node hierarchy
	

	ActivationStatus
	Activation status of the node.
	Possible values are:

· STOPPED

· RUNNING

· FAULT

	ActivationSubStatus
	Additional identifier, documents the ActivationStatus. (Application specific values) 

It identifies specific running behaviors or mitigation methods
	

	OperationalStatus
	Status of the current operational conditions
	Possible values are:

· Normal operation

· Direct manual operation

·  Broken down
· Under maintenance
· Repaired

	SanitaryStatus
	Cleanness, sterility, sanitary Status.
	Possible values are:

· clean

· contaminated

· sterile

· unknown

· Product

	…
	Note : 

Other attributes may be defined by the user
	


Table 7: Node object attributes

These attributes apply to any node whatever is its type.
2.34.2 Node properties

Node properties include the physico-chemical information of the equipment: are configured at the engineering level providing additional, application specific information that describes:

	Example of node properties

	Property Name
	Description
	Examples

	Capacity
	capacity of the equipment
	

	Weight
	
	

	Level
	
	

	Volume
	
	

	DimensionL
	
	

	DimensionW
	
	

	Flow
	Flow of the equipment
	

	Temperature
	Temperature
	

	Pressure
	
	

	PH
	
	

	…
	Note : 

Other attributes may be defined by the user
	


Table 8: Node properties
2.34.3 Node object operations

Any node can have incorporated operations that can be invoked for performing elementary actions.

There are no specifics regarding flow analysis at this level (however, directing nodes have specifics regarding flow control)

2.35 Directing Node object

2.35.1 Directing node object attributes

Directing node object attributes are specific information about this type of nodes
	Directing_Node object attributes

	Attribute Name
	Description
	Possible values

	OperationMode
	The mode of operation is the way the device is controlled. Unlike most methods, flow analysis is concerned by all actuators regardless they are connected to the control system or not.

· 
	Possible values:

· Handled (driven by the operator - no connection with the control system) Ex:A blind flange
· Controlled (driven by the control system). Ex: actuated on-off valve
· Virtual (there are no corresponding device to control). Ex: a glass fiber can be broken at the outlet of the glass oven, corresponding to a “virtual” flow breaker 

	…
	
	


Table 9: Directing node object attributes

2.35.2 Directing node properties
To be completed

	Example of directing node properties

	Property  Name
	Description
	Examples

	
	
	

	
	
	


Table 10: Directing node properties
2.35.3 Directing node operations

Directing nodes actually controls the flow.  It gets information on conditions at its terminals and takes the appropriate protecting decision depending of them.

The Figure 16 shows the different control a directing node is under. Flow control is actually part of the directing node. It acts as an interlock between automatic/manual control and the actuators. 


[image: image17.wmf]Directing node

Automatic

Control

Product

& 

Equipement 

protection

Personnel & 

Environment 

safety

Manual 

Control

Upstream

node

Downstream node

Flow

Flow

Flow

Flow

Control


Figure 16: Directing node control
Directing nodes support the flow analysis safety layer. This safety layer act as an interlock between automatic and manual control, and the actuators within the node. They perform the following flow control operations:

· Set the direction

· Basic control that acts on flow breakers and other actuators

Before establishing a flow

· Control the equipment compatibility

· Check for the invoked terminal relationship if the “open” terminals have compatible statuses with terminals of the connected nodes (a “PayReceive” terminal shall be connected to  either a “MaySend” or a “MaySendOrReceive” terminal  

· Control the flow integrity

· Check if the nodes that will be linked are part of the same flow 

· Control the product-process / equipment compatibility

· Check if the process conditions of the nodes that will be linked are compatible with the equipment capabilities (ex: maximum temperature) and status (ex: clean)

· Control the product-process compatibility

· Check if the products that will be mixed are compatible

When  the flow is estblished

· Control the process conditions against material requirements

· Check if the operating conditions are compatible with the material requirements

To be developed

2.36 Confining node object

2.36.1 Confining node object attributes

To be completed

	Confining_Node object attributes

	Attribute Name
	Description
	Examples

	
	
	

	…
	
	


Table 11: Confining node object attributes

2.36.2 Confining node properties

To be completed

	Example of directing node properties

	Property  Name
	Description
	Examples

	
	
	

	
	
	


Table 12: Confining node properties

2.36.3 Confining node object operations

To be completed

2.37 Complex node object

To be completed

2.37.1 Complex node object attributes

To be completed

2.37.2 Complex node properties

Complex nodes don’t have specific properties. They can be either directing or confining nodes properties.

2.37.3 Complex node object operations
To be completed

2.38 Terminal object

2.38.1 Terminal object attributes

	Terminal object attributes

	Attribute Name
	Description
	Examples

	ID
	An identification of the object.
	

	
	
	

	TerminalStatus
	Status of the terminal regarding the flow that determines if the terminal is or not an end of the flow. An open terminal indicates that the node is part of the flow, but not the last.

A close terminal indicates this node is an end of the flow.
	Possible values are:

· Open

· Close

	FlowStatus
	Status of the terminal regarding the flow. 
	Possible values for a closed terminal: 

· MaySend

· MayReceive

· MaySendOrReceive

Possible values for an open terminal:

· Receiving

· Sending

	…
	
	


Table 13: Terminal object attributes

2.38.2 Terminal properties

To be completed

	Example of terminal properties

	Property  Name
	Description
	Examples

	
	
	

	
	
	


Table 14: Terminal properties
2.38.3 Terminal object operations

To be completed

2.39 Relationship object

Relationships object defines the possible ways through the node. 

These relationships are normally associated with / activated by node operations, which set the different flow breakers (actuators) patterns.

At least one relationship shall be defined for each node. 

Relationship may be active or inactive (at run-time). 

Active relationships determine all actual node internal connections between its terminals. 

If no relationships are active, default relationship apply .

Several relationships may be active at the same time. That means that several separated flows All relationships sharing at least 1 terminal are all connected together.

Example:


[image: image18.wmf]DN

T1

T4

T5

T6

T2

T3


Figure 17 : Internal node relationships
The following table represents all possible Relationships:

	
	Terminal 1
	Terminal 2
	Terminal 3
	Terminal 4
	Terminal 5
	Terminal 6

	RelationShip 1
	
	
	
	
	
	

	RelationShip 2
	
	
	
	
	
	

	RelationShip 3
	
	
	
	
	
	

	RelationShip 4
	
	
	
	
	
	

	RelationShip 5
	
	
	
	
	
	

	RelationShip 6
	
	
	
	
	
	

	RelationShip 7
	
	
	
	
	
	

	RelationShip 8
	
	
	
	
	
	


Table 15: Possible node relationships
For example, relationship 1 lets communicate terminal 1 and 4

2.39.1 Relationship object attributes

Editor’s note

The model only consider simplistic relationships between terminals. More complex relationships regarding physical information transformation (flow, temperature, pressure…) are not taken into account. Is that a problem?
	Relationship object attributes

	Attribute Name
	Description
	Examples

	ID
	An identification of the object.
	

	ActiveStatus
	Flag for the active relationship. 

Several relationship can be active at the same time
	Possible values:

· True

· False

	DefaultRelation
	Identifies the relationship that is enable when no relationships are invoked (i.e. the ActivationStatus of the node is “stopped”, or if the node is not controlled)

Several relationship can be default
	Possible values are

· True

· False


Table 16: Relationship object attributes
2.39.2 Relationship object operations

To be completed

2.40 Terminal configuration object

Terminal configuration set the attributes to all terminals for each identified relationship. The attachment of terminals to relationships must be more 

2.40.1 Terminal configuration object attributes

	Terminal configuration object attributes

	Attribute Name
	Description
	Examples

	TerminalID
	Identification of the terminal
	

	TerminalStatus
	Set the corresponding terminal status.

All unused / blind terminals are set to “Close”. Other are open
	Possible values are:

· Open

· Close

	FlowStatus
	Set the terminal ability  regarding the direction of the flow
	Possible are: 

· MaySend

· MayReceive

· MaySendOrReceive


Table 17: Terminal configuration object attributes

2.40.2 Terminal configuration object operations

To be completed

2.41 Connection object

Connection objects defines links between nodes. It tells a terminal which other terminals from external nodes are connected to it.

I allows the directing node to know the actual conditions in front of each closed terminal, in order to check flow consistency and authorize the corresponding flow breaker to operate. 

2.41.1 Connection object attributes

	Connection object attributes

	Attribute Name
	Description
	Examples

	ID
	An identification of the object.
	

	Terminal1
	First terminal the connection links
	

	Terminal2
	Second terminal the connection links
	


Table 18: Connection object attributes

2.41.2 Connection properties

To be completed

	Example of connection properties

	Property  Name
	Description
	Examples

	
	
	

	
	
	


Table 19: Terminal properties

2.41.3 Connection object operations

To be completed

Implementing flow analysis

This section provides guidance in order to facilitate FA implementation in control systems.

To be completed. 

Editor’s note:

· Shall include an actual example and possibly its implementation.

· Shall address the possible overhead  when implementing the full methodology

· Shall discuss the location of all information attached to the objects (within the PLC/Controller, from an external data-base…) While I thought it was a design / integration only issue, several comments revealed that it is already a concern at our conceptual level
· Shall discuss Internal exception handling































































































































	Page11/45
	28/08/2003
	WBF-WG-FA_Draft3.doc



_1111839939.ppt






Material / Energy 

Sources and sinks

Energy Sources

Energy Sinks

Material Sources

A

D

B

E

F

C



E

nodes

Material / Energy 

Flow vectors





Material Sinks








_1122630563.ppt






CN1

CN2

CN3

CN4

CN5

B1

B2

B3

B4

B5

B6

B7

B8

CN : Confined Nodes

DN : Directing Nodes

B : Flow Breakers

T : Terminals

DN1

DN2

DN3

B9

DN4

DN5

DN6

T1

T2

T1

T2

T1

T2

T1

T2

T3

T1

T2

T3

T4

T1

T2

T3

T1

T2

T1

T2

T1

T2

T1

T2

T1

T2

B10

DN7

T1

T2




























_1123484840.ppt






Nitrogen

Atmosphere

Product in

Product out

N2

N1

N1 : Material/Liquid node

N2 : Material/Gaseous node

Flow break












































_1123509280.ppt






















Directing node

Automatic

Control

Product & Equipement protection

Personnel & Environment safety

Manual Control

Upstream

node

Downstream node

Flow

Flow

Flow

Flow Control














_1123589844.ppt






DN2

T1

T2

T3

T4

B1

DN1

T1

T2

B1

DN2

T1

T2

B1

DN3

T1

T2








_1123589936.ppt






DN

T1

T4

T5

T6

T2

T3








_1123489596.ppt


















Ny2

Ny6

Ny3

Ny5

Ny4

Ny1

T3













Nx1

T1

T2

T3













Nx2

T1

T3

T2

T4

T5

T1

T2

Nz1








_1123429010.ppt






CN1

T1

T2

CN2

T1

T2

T3

B1

DN3

T1

T2

Node 

  Actual Pressure = 1.12 Bar  

  Actual Temp = 65C

  Actual Product = Water

  Actual Quantity = 255 L



  Design Pressure = 2.2 Bar

  Design Temperature = 120C

  Capacity = 855 L

Output Terminal

T2_Conditions = CN1_Condition

Input Terminal

Status=Blocked

T1_Conditions = T2_Conditions

Connection

T3.CN1 => T1DN3

Output Terminal

Status=Blocked

T2_conditions 	= CN2.T1_Condition

	= CN2_conditions

Connection

T3.CN1 => T1DN3

Node 

  Actual Pressure = 1.00 Bar  

  Actual Temp = 25C

  Actual Product = Water

  Actual Quantity = 0 L



  Design Pressure = 6 Bar

  Design Temperature = 120C

  Capacity = 0 L

Output Terminal

Connected terminal DN3.T2=Blocked =>

T1_Conditions = CN2_Condition

CN1

DN3

CN2

Actual condition 1

Actual condition 2






















_1122638132.ppt






N1

N2

N4

N3

B1

B2

B3

B4

B5

B6

B7

B8

N : Nodes

B : Flow Breakers

T : Terminals

B9

T1

T2

T2

T1

T3

T3

T4

T5

T3

T1

T1

T1

T2

B10

T2




























_1122630466.ppt






B2

B3

B4

DN2

T1

T2

T3

T4








_1122630491.ppt






Node

Terminals

Node

Connection








_1122630354.ppt






CN1

T1

T2

T3

CN2

T1

T2

T3






















_1122469056.ppt






Raw material storage area

Power

Water

Raw

Materials

Heat

Smoke

Waste water

Finished

goods

Power generation and utility distribution

Process cell 1

Finished goods storage area

Fuel

Waste collection and disposal

Process cell 1








_1111755225.ppt






Material / Energy 

Sources and sinks

Energy Sources

Energy Sinks

Material Sources

A

D

B

E

F

C



E

Nodes

Material / Energy 

Flow vectors





Material Sinks








_1111755264.ppt






Material / Energy 

Sources and sinks

Energy Sources

Energy Sinks

Material Sources

A

D

B

E

F

C



E

 nodes

Material / Energy 

Flow vectors

P1

P1

P1

P1





Material Sinks








_1073472545.ppt






T1

T2

T3

T4

T5

T6

T7

T8

Vi1

Vi3

Vi2

Vi4

Vi5a

Vi6a

Vo1a

Vi7a

Vi8a

Vi5b

Vi6b

Vi7b

Vi8b

Vo1b

Vo2a

Vo2b

Vo3a

Vo3b

Vo4a

Vo4b



PA



























































PB






































































